## COVER
Date:
Rev. Date:
City of Chicago
Department of Water Management
Stormwater Spreadsheet Tool
Release 5.1 effective 02-01-2025
1. DOB Tracking/Permit Number:
2. Name of Project:
3. Address of Site:
Architect / Engineer of Record:
Phone No.:
4. Description of Proposed Work:
5. Use of Building (if applicable):
6. Sewer Altas & Drain Atlas Referenced:
7. Site Area:
|  |  | sq ft | acres
8. Project Area:
|  |  | sq ft | acres
9. Chicago Sustainable Development Policy:
Does this project exceed the minimum requirements of the Stormwater Ordinance in order to comply with the Chicago Sustainable Develoment Policy?
|  | No | (Answer Yes or No)
This spreadsheet tool has been prepared to assist the applicant in preparing calculations
for simple sites. The applicant is responsible for ensuring that submitted calculations are
correct. If necessary, supporting hand calculations should be prepared and submitted.
Color Coding
- Cell Contents Computed by Spreadsheet
- Cell for User Entry
- Cell Includes Comment (when cursor is over it)
Note on C58: When red triangle in upper right corner of cell is present, comment will appear when cursor is held over box.

## INDEX
City of Chicago
Department of Water Management
Stormwater Spreadsheet Tool
INDEX OF SPREADSHEETS
| Required>> | X | COVER
| Required>> | X | INDEX
0.0 RELEASE RATE
| Required>> | X | 1.0 RATE CONTROL
1.1 Dry Weather Flow
1.2 BMPs-Rate Control Credit
|  | X | 1.3 Restrictor Sizing
| Required>> | X | 2.0 VOLUME CONTROL
2.1 BMP Volume Summary
2.1.1 Bioinfiltration
2.1.2 Drainage Swales
2.1.3 Green Roof
2.1.4 Infiltration Vault
2.1.5 Trees
2.1.6 Permeable Pavement
2.1.7.1 Roof Runoff BMPs - Planter Boxes
2.1.7.2 Roof Runoff BMPs - Rain Barrels / Cisterns
2.1.8 Filter Strips
2.1.9 Oversized Detention
3.0 SUSTAINABLE DEVELOPMENT POLICY
3.1 Exceed Rate Control
3.2 Exceed Volume Control

## 0.0 RELEASE RATE
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
0.0 Release Rate
Step 1: Sewer Capacity of Each Sewer Segment
Sewer Segment: | Segment 1 | Segment 2 | Segment 3 | Segment 4 | Segment 5 | Segment 6
Street Name:
Upstream End (street name):
Downstream End (street name):
Upstream Invert (ft):
Downstream Invert (ft):
Pipe Segment Length (ft):
Pipe Slope (S):
Pipe Characteristics:
Pipe Size (in):
Pipe Area (sq ft): | 0 | 0 | 0 | 0 | 0 | 0
Wetted Perimeter (ft): | 0 | 0 | 0 | 0 | 0 | 0
Hydraulic Radius (ft):
Roughness Coefficient (n):
Flow Conveyance (K):
Manning's Equation: | [6 empty] | The Mannings Equation cannot be used to analyze a pipe with zero or negative slope.
Velocity (fps):
Hydraulic Capacity (cfs):
Roughness Coefficient (n):
VCP: use 0.011, | typical for pipe <= 21 in
RCP: use 0.013, | for pipe >=24 in when pipe size shown on atlas in inches
brick sewer: use 0.015, | for pipe >=24 in when pipe size shown on atlas in feet
Step 2: Tributary Area to Each Sewer Segment
|  | Segment 1 |  |  | Segment 2
Total Tributary Area (ac): |  | Adj. Factor | Adjusted Area |  | Adj. Factor | Adjusted Area
Residential Area (ac): | 0 | 1 | 0 | 0 | 1 | 0
Commercial Area (ac): |  | 1.3 | 0 |  | 1.3 | 0
Industrial Area (ac): |  | 1.5 | 0 |  | 1.5 | 0
|  | Total Adjusted Area: | 0 |  | Total Adjusted Area: | 0
|  | Segment 3 |  |  | Segment 4
Total Tributary Area (ac): |  | Adj. Factor | Adjusted Area |  | Adj. Factor | Adjusted Area
Residential Area (ac): | 0 | 1 | 0 | 0 | 1 | 0
Commercial Area (ac): |  | 1.3 | 0 |  | 1.3 | 0
Industrial Area (ac): |  | 1.5 | 0 |  | 1.5 | 0
|  | Total Adjusted Area: | 0 |  | Total Adjusted Area: | 0
|  | Segment 5 |  |  | Segment 6
Total Tributary Area (ac): |  | Adj. Factor | Adjusted Area |  | Adj. Factor | Adjusted Area
Residential Area (ac): | 0 | 1 | 0 | 0 | 1 | 0
Commercial Area (ac): |  | 1.3 | 0 |  | 1.3 | 0
Industrial Area (ac): |  | 1.5 | 0 |  | 1.5 | 0
|  | Total Adjusted Area: | 0 |  | Total Adjusted Area: | 0
Note: Total tributary areas entered for segments 1 through 6 must include the cumulative tributary area for each segment. All upstream tributary areas must be included.
Step 3: Determine Release Rates of Each Segment
| Segment 1 | Segment 2 | Segment 3 | Segment 4 | Segment 5 | Segment 6
Release Rate (cfs/ac):
|  | Critical Local Sewer Capacity (cfs/ac): | 0
Step 4: Compare Outlet Sewer Capacity and Determine Release Rate
Name of Outlet Drainage Basin (as shown on the map):
Outlet Sewer Capacity (cfs/ac):
|  | Maximum Allowable Release Rate (cfs/ac): | 0
Note on E64: DC5700-XPPRO: Insert outlet sewer capacity from Outlet Sewer Capacity Map, Effective Jan 1, 2010 or latest revision

## 1.0 RATE CONTROL
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
1.0 Rate Control (Sheet 1 of 2)
Step 1: | Runoff Calculation |  | Proposed Area (sq ft) | C-Value 100-Year | Storage Volume (cu ft)
| Pervious Land | Lawns - Sandy soil, flat, 0% to 2% |  | 0.18 | 0
|  | Lawns - Sandy soil, avg, 2% to 7% |  | 0.27 | 0
|  | Lawns - Sandy soil, steep, >7% |  | 0.36 | 0
|  | Lawns - Heavy soil, flat, 0% to 2% |  | 0.3 | 0
|  | Lawns - Heavy soil, avg, 2% to 7% |  | 0.42 | 0
|  | Lawns - Heavy soil, steep, >7% |  | 0.47 | 0
|  | Woodlands, flat, 2% |  | 0.39 | 0
|  | Native Vegetation with prepared soils |  | 0.1 | 0
|  | Dry bottom basins to HWL |  | 0.75 | 0
|  | Wetland |  | 0.8 | 0
|  | Green Roof |  | 0.5 | 0
| Impervious Land | Gravel |  | 0.7 | 0
|  | Pavement |  | 0.95 | 0
|  | Roofs (conventional) |  | 0.95 | 0
|  | Critical building sidewall (enter 25% of the face of the largest sidewall draining to lower level roofs or side gutters) |  | 0.95 | 0
|  | Wet bottom basins to HWL |  | 1 | 0
| BMP areas | BMPs providing storage that WILL COUNT toward detention storage (from Worksheet 1.2) | 0 | 1
|  | BMPs providing volume control storage that WILL NOT BE COUNTED toward detention (from Worksheet 1.2) | 0 | Storage Provided will be used to factor the adjusted C-value in Cell D38 | 0
| Summary | Total pervious area | 0 | sq ft
|  | Total impervious area | 0 | sq ft
|  | Total BMP area | 0 | sq ft
|  | Total project area including sidewall | 0 | sq ft | 0 | acres
|  | Total project area excluding sidewall | 0 | sq ft | 0 | acres
|  | Weighted C- value (non BMP areas) | 0 | unitless
|  | Adjusted C-value (including BMPs) | 0 | unitless
|  | Notes: | Make note of any adjustments made for purposes of detention calcs here (such as removal of roof area that will discharge directly to Waters)
Step 2: | Allowable Release Rate Assessment |  |  | Type Yes or No for all that apply | Notes
| Question 1: | Does the site drain directly to Waters?
| Question 2: | Does the site only include residential land use?
| Question 3: | Is the Regulated Development a Lot-to-Lot Buillding (85% or more of site footprint is occupied by buildings)?
| Question 4: | Do you plan to use the standard maximum release rate (only available to sites less than 1.75 acres)?
| Question 5: | Is the site more than 75 percent of substantially contiguous at-grade open space that is conducive to ponding of surface waters (Answer "No" if site discharges to waterway or is a service station)?
| Question 6: | Does the development involve flow diversions (existing sewer connection to be relocated to a different main) or multiple sewer connections (only available to sites over 1.75 acres)?
| Question 7: | Are there widespread contaminated soils on the site, high ground water table, or is this development classified as a lot-to-lot building?
City of Chicago
Department of Water Mangement
Name of Project:
Address:
A/E of Record:
1.0 Rate Control (Sheet 2 of 2)
Step 3: | Achieving Rate Control Measures
| Unadjusted Detention Release Rate | 0 | cfs | Waiting for Answer to Question 1 and 4 |  | 0
| Average Dry Weather Flow Rate (From Tab 1.1) | 0 | cfs | Waiting for Dry Weather Flow worksheet to be completed
| Infiltration Facility Release Rate | 0 | cfs | No BMPs with infiltration beds entered on BMP Summary Worksheet or soil's infiltration rate is less than 0.5 in/hr
| Release rate for detention storage computations | 0 | cfs
| Required Storage Volume | 0 | cu ft
Detention Storage Calculations
(Based on Bulletin 75 Rainfall Data)
STORM EVENT (5,10,25,50 or 100) =
|  | 100 |  | Allowable release rate |  | 0 | cfs
|  |  |  | Inflow |  | Release | Storage | Storage
Storm | Runoff | Rainfall | Drainage | Rate | Total | Rate | Rate | Volume Rate
Duration | Coefficient | Intensity | Area A | Q=CIA | Storm Vol | Qo | Qi-Qo | (Qi-Qo)*t*60
(minutes) | C | (in/hr) | (acres) | (cfs) | (cu ft) | (cfs) | (cfs) | (cu ft)
5 | 0 | 12.36 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 9.28 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 6.34 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 4.03 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0 | 2.485 | 0 | 0 | 0 | 0 | 0 | 0
180 | 0 | 1.83 | 0 | 0 | 0 | 0 | 0 | 0
360 | 0 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0
720 | 0 | 0.62167 | 0 | 0 | 0 | 0 | 0 | 0
1080 | 0 | 0.44778 | 0 | 0 | 0 | 0 | 0 | 0
1440 | 0 | 0.35708 | 0 | 0 | 0 | 0 | 0 | 0
2880 | 0 | 0.19333 | 0 | 0 | 0 | 0 | 0 | 0
4320 | 0 | 0.13681 | 0 | 0 | 0 | 0 | 0 | 0
7200 | 0 | 0.088833 | 0 | 0 | 0 | 0 | 0 | 0
14400 | 0 | 0.052708 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Required Detention Volume (cu ft) | 0
Note: 1) the calculation assumes that the rising and recessing limb of inflow and outflow hydrograph are vertical
Note on C65: If infiltration rate is greater than 0, will be added to detention release rate for purposes of detention volume sizing
Note on C66: This rate used below in Cell G73 to compute maximum required storage
Note on C72: User must enter appropriate design storm. In most cases, the 100-year event will apply, but reduced standards apply to special cases such as lot-to-lot buildings and residential developments
Note on D13: Submit geotechnical report to substantiate the presence of sandy soil
Note on D14: Submit geotechnical report to substantiate the presence of sandy soil
Note on D15: Submit geotechnical report to substantiate the presence of sandy soil
Note on D27: Building sidewall area is counted as part of the site area for calculating required detention volume but is not counted toward the allowable release rate.
Note on D29: From 1.2 BMPs - Rate Control Credit
Note on D30: From 1.2 BMPs - Rate Control Credit
Note on D34: Does include building sidewalls.
Note on D36: The combination of pervious area, impervious area, and BMP area should add up to the total site area.
Note on D39: Accounts for BMPs with C-value of 1.0 (cells D29 and E29) or for BMPs providing storage (cells D30 and F30) BMP C-value is limited to 0.10 minimum
Note on E23: Green Roof C-Values= 0.5 for <4" depth 0.3 for 4"-8" depth 0.2 for 9"-20" depth 0.1 for >20" depth
Note on E29: Set to 1.0 for all BMPs except permeable pavement ( uses 0.95 due to interception on surface and in bedding that isn't credited on worksheet) because storage will be fully counted toward detention and surface is treated like a wet pond
Note on E48: Do not answer this question (you can type "see Q1") if answer to Question 1 is yes and you intend to use release rate of 1 cfs/acre
Note on F30: From 1.2 BMPs - Rate Control Credit

## 1.1 Dry Weather Flow
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
1.1 Dry Weather Flow
Average Dry Weather Flow
To be used to determine if the allowable release rate for detention storage must be lowered to account for a significant DWF (DWF > 10% of the allowable release rate).
Land Use | Average Gallons per Day (gpd) |  | Quantity | Average Dry Weather Flow
Hospitals | 250 | per bed space |  | 0 | cfs
Hotels (w/laundry) | 150 | per room |  | 0 | cfs
Hotels (w/o laundry) | 60 | per room |  | 0 | cfs
Single Family | 350 | per home |  | 0 | cfs
Multi-Family - 3 bedroom | 300 | per unit |  | 0 | cfs
Multi-Family - 2 bedroom | 300 | per unit |  | 0 | cfs
Multi-Family - 1 bedroom | 150 | per unit |  | 0 | cfs
Studio Apartment | 100 | per unit |  | 0 | cfs
Boarding Homes | 50 | per person |  | 0 | cfs
Factories (excluding process water) | 35 | per person, per shift |  | 0 | cfs
Office | 15 | per person, per shift |  | 0 | cfs
Restaurant (w/ lounge) | 12 | per patron |  | 0 | cfs
Restaurant (w/o lounge) | 10 | per patron |  | 0 | cfs
Convention Center | 5 | per patron |  | 0 | cfs
|  |  | Total | 0 | cfs
|  | Equivalent Drainage Area |  | 0 | sq ft
Peak Dry Weather Flow
To be used for sewer connection sizing and surcharge calculations
The DWF (with peaking factor) should be based on the number of fixture units (FTU), reference the Municipal Building Code, Table 18.29-1108.1. The conversion from the number of fixture units to drainage area (sf) to peak DWF (cfs) is as follows:
Drainage area | = [(FTU – 150) * 7.2] + 4850 sf
Peak DWF | = Drainage Area / 43,560 sf/acre * 1.0 cfs/acre
Building Fixture Units |  | FTU
Equivalent Drainage Area |  | sq ft
Peak DWF |  | cfs

## 1.2 BMPs-Rate Control Credit
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
1.2 BMPs for Rate Control Credit
Volume Control BMP Summary for use in Rate Control Worksheet
Instructions for use:
This summary worksheet provides information for BMPs for use in the Rate Control Spreadsheet.
Storage provided should be from the computation made on the each individual BMP spreadsheet (2.1.1 to 2.1.8).
Total area of BMPs will carry over to Rate Control Worksheet.
Other areas (ie reduce pavement area if permeable pavement implemented)should adjusted such that Line 35 on Rate Control Worksheet equals total site area.
When the option exists, the applicant may decide whether or not to count volume control storage toward detention storage.
n/a = not applicable and indicates when credit is inappropriate or unavailable for a given BMP.
BMP Areas with Storage COUNTED toward Rate Control Volume
| Type "yes" to Select | BMP | BMP Infiltration Area (sq. ft.) | Storage Provided (cu. ft.) | Design Soil Infiltration Rate (in/hr) 3 | Allowable Infiltration Release Rate (cfs)
|  | Bioinfiltration Systems | 0 | 0 | 0 | 0
|  | Drainage Swales | 0 | 0 | 0 | 0
| n/a | Green Roof | n/a | n/a | n/a | n/a
|  | Infiltration Vault | 0 | 0 | 0 | 0
| n/a | Natural Landscaping and Stormwater Trees1 | n/a | n/a | n/a | n/a
|  | Roof Runoff BMPs - Planter Boxes | 0 | 0 | 0 | 0
|  | Roof Runoff BMPs - Rain Barrels and Cisterns | n/a | 0 | n/a | n/a
|  | Permeable Paving | 0 | 0 | 0 | 0
| n/a | Vegetated Filter Strips2 | n/a | n/a | n/a | n/a
|  | Totals | 0 | 0 | - | 0
Notes:
1. Natural landscaping areas do not have specific storage, they can simply be entered on Rate Control Spreadsheet as having a C-value of 0.1. Detention Credit is not given for stormwater trees.
2. Vegetated Filter strips also are not given credit for a "volume of storage" and should be entered in the pervious land cover section of the Rate Control Spreadsheet based on their cover type.
3. Infiltration rate must be the design infiltration rate as explained in Stormwater Manual. If the infiltration rate is less than 0.5 in/hr, credit cannot be taken for infiltration and the Allowable Infiltration Release is set to zero. This value is automatically copied from each respective BMP spreadsheet.
BMP Areas with Storage NOT COUNTED toward Rate Control Volume
| Type "yes" to Select | BMP | Area (sq. ft.) | Storage Provided (cu. ft.)
|  | Bioinfiltration Systems | 0 | 0
|  | Drainage Swales | 0 | 0
| n/a | Green Roof | n/a | n/a
| n/a | Natural Landscaping and Stormwater Trees1 | n/a | n/a
|  | Roof Runoff BMPs - Planter Boxes | 0 | 0
|  | Permeable Paving | 0 | 0
| n/a | Vegetated Filter Strips2 | n/a | n/a
|  | Totals | 0 | 0
Note on B22: User will typically want to apply storage toward Rate Control Credit, so type yes here. In some cases if BMP is being used as a permeable surface (to meet impervious surface reduction requirement), then user may wish to treat solely as a permeable surface. In that case enter "yes" in lower section (see line 41) instead.
Note on B42: In some cases if BMP is being used as a permeable surface (to meet impervious surface reduction requirement), then user may wish to treat solely as a permeable surface. In that case enter "yes" here instead of upper section.
Note on D25: This number comes from the Volume Control Spreadsheet which only accounts for storage up to a depth of 6-inches. Storage above 6-inches under the design rate control event (i.e. 100-yr storm event) should be separately accounted for in Detention Storage calculations, if applicable.
Note on D33: Used in Rate Control Worksheet Cell D28
Note on D45: This number comes from the Volume Control Spreadsheet which only accounts for storage up to a depth of 6-inches. Storage above 6-inches under the design rate control event (i.e. 100-yr storm event) should be separately accounted for in Detention Storage calculations, if applicable.
Note on D51: Used in Rate Control Worksheet Cell D29
Note on E51: Used in Rate Control Worksheet Cell F29
Note on F22: Infiltration rate must be as measured in field as explained in Stormwater Manual, Factor of Safety of 2 will be applied when providing credit toward detention release.
Note on G22: If Infiltration is below 0.5, then the allowable infiltration is set to zero.

## 1.3 Restrictor Sizing
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
1.3 Restrictor Sizing
|  |  |  | Type Yes or No | Notes
| Question 1: | Does the design include Oversized Detention with an associated reduction in the allowable release rate?
| Question 2: | Does the design exceed the Stormwater Ordinance requirements by achieving strategy 3.1 or 3.2 of the Sustainable Development Policy with an associated reduction in the allowable release rate?
This worksheet takes the allowable release rate from Tab 1.0 (typically) or Tab 2.1.9 (for Oversized Detention) or Tab 3.1 (for Exceeding the Stormwater Ordinance to meet the Sustainable Development Policy), and sizes an orifice to provide this peak discharge rate. Discharge through infiltration is not included when sizing the restrictor.
Summary of Release Rates:
| Release Rate from Tab 1.0 Rate Control |  | Q | 0 | cfs
| Release Rate from Tab 2.1.9 Oversized Detention |  | Q |  | cfs
| Release Rate from Tab 3.1 Exceed Rate Control |  | Q |  | cfs
| Controlling (Smallest) Release Rate |  | Q | 0 | cfs
Restrictor Head Calculation (for both Orifice Plate and Vortex Restrictors):
| 100-Year High Water Level |  | HWL | 20 | feet
| Upper Invert of Half-Trap |  |  | 16 | feet
| Calculated Head |  | h | 4 | feet
Orifice Plate Sizing Calculation:
This calculation is used to size the appropriate diameter orifice in a steel plate. See Sewer Detail A-19.
| General Formula: | Q = CdA(2gh)^0.5
| Where: | Cd = 0.61 for sharp-edged plate bolted to a catch basin
Cd = 0.82 for pipes less than 2 feet long grouted into sewer
| Orifice Description: |  |  | Orifice Plate
| Discharge |  | Q | 0 | cfs
| Discharge coefficient |  | Cd | 0.61 | unitless
| Calculated Head |  | h | 4 | feet
| Orifice Diameter |  | d |  | inches
Specify a Vortex Restrictor:
| Calculated Head |  | h | 4 | feet
| Release Rate for Vortex Restrictor |  | Q |  | cfs

## 2.0 VOLUME CONTROL
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.0 Volume Control
Step 1: | Runoff Calculation |  | Existing Area (sq ft) | Proposed Area (sq ft)
| Pervious Surface or Land Cover not Counted as Impervious for Volume Control Calculations | Bare Earth
Lawn or Landscaped Areas
Woodlands
Wetland
| Impervious Land | Gravel
Pavement
Roofs (conventional)
Water (including Wet Bottom Basin to HWL)
| BMPs | Green Roof | -
|  | Permeable Pavement | -
|  | Bioinfiltration | -
|  | Swales | -
|  | Stormwater Trees | -
|  | Roof Runoff Planters | -
|  | Filter Strips | -
|  | Dry Bottom Basins to HWL | -
| Summary | Total pervious area (sq ft) | 0 | 0
|  | Total impervious area (sq ft) | 0 | 0
|  | Total BMP areas treated as impervious area (sq ft) | - | 0
|  | Total BMP areas treated as pervious area (sq ft) | - | 0
|  | Total site area (sq ft) | 0 | 0
|  | Imperviousness percentage (%) | 0 | 0
Step 2: | Volume Control Assessment
|  | Type Yes or No for all that apply | Note
Question 1: | Does the site drain directly to Waters?
Question 2: | Are infiltration BMPs allowable? (See Chapter III Sections 4.1.2 of the Regulations.)
Question 3: | Do you wish to use permeable pavement only as a pervious surface to achieve impervious surface reduction goal?
Step 3: | Achieving Volume Control Measures
Achieve I. or II. below in accordance with the Ordinance.
I. | Capture 0.5" of runoff from impervious surfaces. Storage required = | 0 | cubic feet | Go to spreadsheet 2.1 BMP Volume Summary if electing volume control storage option
or, II. | Reduce proposed imperviousness to: | - | percent
Note on B17: Tributary sidewalls are not required as part of volume control computations, thus, no space is allotted for its entry on this worksheet.
Note on E19: Roofs that discharge directly to waters may be ommitted from the volume control calculations. Complete worksheet for remainder of site.
Note on E21: Green roof will be counted as pervious surface for reduction of site imperviousness.
Note on E22: Permeable paving can either be counted as pervious surface for reduction of site imperviousness, or included as an impervious surface in the calculation of required volume control storage. (See question 3 below)
Note on E23: Any area for stormwater trees entered here may be subtracted from the nearby impervious surface. See Stormwater Trees Worksheet.
Note on E35: Compare with Cell C49 to see if requirements are met.

## 2.1.1 Bioinfiltration
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.1 Bioinfiltration Systems
Section 1 Upstream Drainage Area
| 1 | Upstream impervious area including BMP area | At |  | square feet
| 2 | Upstream weighted C-value (C-value=1.0 for bioinfiltration area for direct rainfall) | C | 1 | unitless
| 3 | Volume of upstream runoff from a 1-inch storm = C * At * 1/12 | Vupstream | 0 | cubic feet
| 4 | Describe upstream drainage area
| 5 | Describe upstream pretreament or integration of pretreatment into BMP
Section 2 BMP Feasibilty
| 6 | Design soil infiltration rate (underdrain system is required if infiltration rate is less than 0.5 in/hr) | i |  | in/hr
| 7 | Elevation of bottom of BMP (the infiltration surface) IF there is no underdrain, OR the lowest underdrain invert elevation | ELEVBMP |  | feet
| 8 | Groundwater elevation | ELEVGW |  | feet
| 9 | Depth to seasonal groundwater (Must be 2 feet or greater, or 3.5 feet or greater if draining to combined sewer) | DGW | 0 | feet
Section 3 BMP Specifications
| 10 | Dimensions of the bioinfiltration facility (length, width, or area) | L |  | feet
|  |  | W |  | feet
|  |  | ABMP |  | square feet
| 11 | Depth of prepared soil | D1 |  | feet
| 12 | Prepared soil porosity (0.25 maximum unless detailed materials report provided) | P1 |  | unitless
| 13 | Depth of underlying aggregate (optional) | D2 |  | feet
| 14 | Aggregate porosity (0.38 maximum unless detailed materials report provided) | P2 |  | feet
| 15 | Surface storage volume (provide supporting calculations, max depth 12 inches) | VAIR |  | cubic feet
| 16 | Soil media storage volume = ABMP * [(D1 * P1) + (D2 * P2)] | VSOIL | 0 | cubic feet
Section 4 BMP Performance
| 17 | Volume of upstream runoff (Line 4) | Vupstream | 0 | cubic feet
| 18 | Storage Provided = VAIR + VSOIL | VBMP | 0 | cubic feet
| 19 | Vtotal (equals lesser of VBMP or Vupstream) | Vtotal | 0 | cubic feet

## 2.1.2 Swales
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.2 Drainage Swales
Section 1 Upstream Drainage Area
| 1 | Upstream impervious area including BMP area | At |  | square feet
| 2 | Upstream weighted C-value (C-value=1.0 for bioinfiltration area for direct rainfall) | C |  | unitless
| 3 | Volume of upstream runoff from a 1-inch storm = C * At * 1/12 | Vupstream | 0 | cubic feet
| 4 | Time of Concentration for upstream area (use TR-55 or DWM approved method) | Tc |  | minutes
| 5 | 2-year Rain Intensity based on Tc (see chart) | I |  | in/hr
| 6 | 2-Year Design Flow: Q = C*I*Au/43560 | Q2 |  | cfs
| 7 | Describe upstream drainage area
Section 2 BMP Feasibilty
| 8 | Design soil infiltration rate (underdrain system is required if infiltration rate is less than 0.5 in/hr) | i |  | in/hr
| 9 | Elevation of bottom of BMP (the infiltration surface) IF there is no underdrain, OR the lowest underdrain invert elevation | ELEVBMP |  | feet
| 10 | Groundwater elevation | ELEVGW |  | feet
| 11 | Depth to seasonal groundwater (Must be 2 feet or greater, or 3.5 feet or greater if draining to combined sewer) | DGW | 0 | feet
Section 3 BMP Specifications
| 12 | Dimensions of the drainage swale [length L, side slope SS, bottom width (BW), swale flowline Slope, Manning's n] | L |  | feet
|  |  | SS |  | ft/ft
|  |  | BW |  | feet
|  |  | Slope (0.5% to 2.5%) |  | %
|  |  | Manning n |  | unitless
| 13 | Depth of Flow (must be 6 inches or less) | 2-Year Depth of Flow |  | inches
| 14 | Check to see if selected depth can pass 2-year flow (result must be greater than or equal to 2-year flow in line 8) Q = 1.49/n*A*(R^0.67)*(S/100)^0.5 | Qswale | #DIV/0! | cfs
| 15 | Velocity at 6-inch depth of flow | Vel | #DIV/0! | ft/sec
| 16 | Check dam height (max = 1 foot) | Hdam |  | ft
| 17 | Check dam area = BW*Hdam+SS*Hdam^2 | Adam | 0 | square feet
| 18 | Spacing of dams = Hdam/Slope | Spacing | #DIV/0! | ft/dam
| 19 | Total number of check dams = L/Spacing (round down) | Ndam | #DIV/0! | dams
| 20 | Check dam storage = Ndam*Adam*Spacing/2 | Vdam | #DIV/0! | cubic feet
| 21 | Depth of prepared soil | Dsoil |  | feet
| 22 | Prepared soil porosity (0.25 maximum unless detailed materials report provided) | Psoil |  | unitless
| 23 | Soil storage volume = L*BW*Dsoil*Psoil | Vsoil | 0 | cubic feet
| 24 | Depth of underlying aggregate (optional, provision of aggregrate only allowed when minimum infiltration feasibility requirements are met or when underdrains are provided) | Dagg |  | feet
| 25 | Width of aggregate layer | Wagg |  | feet
| 26 | Aggregate porosity (0.38 maximum unless detailed materials report provided) | Pagg |  | unitless
| 27 | Aggregate storage volume = L*Wagg*Dagg*Pagg | Vagg | 0 | cubic feet
Section 4 BMP Performance
| 28 | Volume of upstream runoff (Line 4) | Vupstream | 0 | cubic feet
| 29 | Check Dam Storage (Line 21) | Vdam | #DIV/0! | cubic feet
| 30 | Soil Storage (Line 24) | Vsoil | 0 | cubic feet
| 31 | Aggregate Storage (Line 28) | Vagg | 0 | cubic feet
| 32 | Storage Provided = Vdam + Vsoil + Vagg | VBMP | #DIV/0! | cubic feet
| 33 | Vtotal (equals lesser of VBMP or Vupstream) | Vtotal | 0 | cubic feet
Note on E16: Includes 75% adjustment factor for use of 100-year C-value with 2-year design flow computation
Note on E27: Ratio of Horizontal distance to Vertical change. (i.e. 3 ft/ft has 3 ft of horizontal change to 1 ft of vertical change)
Note on E30: Use Manning's n = 0.15 for depth of 0 to 4 inches 0.135 for depth of 5 inches 0.12 for depth of 6 inches
Note on E32: Channel slope will need to be 1.6% or less to meet minimum velocity criteria at 6-inch depth. Computed flow must be equal to or greater than 2-year flow
Note on E33: Must be less than 1 ft/sec

## 2.1.3 Green Roof
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.3 Green Roof
Section 1 BMP Specifications
| 1 | Dimensions of the green roof (length L, width W, substrate thickness T) | L |  | feet
|  |  | W |  | feet
|  |  | T |  | inches
Section 2 BMP Performance
Volume control when green roof treated as a pervious surface
| 2 | Green roof counted toward pervious area (check to see if overall site imperviousness reduction is greater than 15 percent, if so volume control requirements have been met) | AG | 0 | square feet
Note on E18: Override this factor if green roof is an irregular shape.

## 2.1.4 Infiltration Vault
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.4 Infiltration Vault
Section 1 Upstream Drainage Area
| 1 | Upstream impervious area | Ai |  | square feet
| 2 | Upstream weighted C-value | C |  | unitless
| 3 | Volume of upstream runoff from a 1-inch storm = C * At * 1/12 | Vupstream | 0 | cubic feet
| 4 | Describe intended function of system (Is it standalone system designed for infiltration, is it integrated as part of the detention storage?)
Section 2 BMP Feasibilty
| 5 | Design soil infiltration rate (must be 0.5 in/hr or greater) | i |  | in/hr
| 6 | Allowable depth of storage (distance below outflow invert plus depth of storage aggregate) = (i / 12 inches/ft * 48 hours) | Dallow | 0 | feet
| 7 | Elevation of bottom of BMP (the infiltration surface) | ELEVBMP |  | feet
| 8 | Groundwater elevation | ELEVGW |  | feet
| 9 | Depth to seasonal groundwater (Must be 2 feet or greater, or 3.5 feet or greater if draining to combined sewer) | DGW | 0 | feet
Section 3 BMP Specifications
| 10 | Dimensions of the infiltration area (length, width, or area) | L |  | feet
|  |  | W |  | feet
|  |  | ABMP | 0 | square feet
| 11 | Depth of open storage (distance between vault outflow invert and top of aggregate/infiltration bed (D1 plus D2 must be less than Dallow) | D1 |  | feet
| 12 | Depth of underlying aggregate | D2 |  | feet
| 13 | Aggregate porosity (0.38 maximum unless detailed materials report provided) | P2 |  | unitless
| 14 | Storage applicable to volume control = (ABMP * D1)+(ABMP * D2 * P2) | VBMP | 0 | cubic feet
Section 4 BMP Performance
| 15 | Volume of upstream runoff (Line 3) | Vupstream | 0 | cubic feet
| 16 | Volume Control Storage Provided = VBMP | VBMP | 0 | cubic feet
| 17 | Vtotal (equals lesser of VBMP or Vupstream) | Vtotal | 0 | cubic feet

## 2.1.5 Trees
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.5 Stormwater Trees
Section 1 Impervious Areas and Trees
| 1 | List impervious surfaces that will be effectively reduced by implementation or preservation of trees | Area (sf) | Number of new trees within 20 feet | Number of existing Trees within 20 feet | Total canopy size of existing trees | Area of Trees (New trees * 50 sf + existing tree canopy *0.5) | Effective Impervious Area for Volume Control = (Area - Trees Area)
|  | Gravel |  |  |  |  | 0 | 0
|  | Pavement |  |  |  |  | 0 | 0
|  | Ponds or wet bottom basins to HWL |  |  |  |  | 0 | 0
Section 2 Detailed Tree Listing
| 2 | List trees and attach plan showing location and sizes of all proposed trees (Attach additional sheets if necessary) | Species | Caliper at 4.5 feet (must be >2 inch) | 50% Canopy size (use 50 sq. ft. max)
| 3 | List trees and attach plan showing location and sizes of all trees to be preserved (Attach additional sheets if necessary) | Species | Caliper at 4.5 feet (must be >4 inch) | Existing Canopy (sf)
Note on I11: May use this new effective impervious area on the volume control spreadsheet

## 2.1.6 Permeable Pavement
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.6 Permeable Pavement
Section 1 Upstream Drainage Area
| 1 | Upstream impervious area including area of permeable pavement | Ai |  | square feet
| 2 | Upstream weighted C-value (C-value=0.95 for permeable pavement areas for nearly direct rainfall) | C | 0.95 | unitless
| 3 | Volume of upstream runoff from a 1-inch storm = C * At * 1/12 | Vupstream | 0 | cubic feet
| 4 | Describe intended function of system (Is it standalone system designed for infiltration, is integrated as part of the detention storage, is it underdrained to downstream system, will it receive upstream runoff?)
Section 2 BMP Feasibilty
| 5 | Design soil infiltration rate (underdrain system is required if infiltration rate is less than 0.5 in/hr) | i |  | in/hr
| 6 | Allowable depth of storage aggregate without provision of underdrain (=i/ 12 inches/ft * 48 hours) | Dallow | 0 | feet
| 7 | Elevation of bottom of BMP (the infiltration surface) IF there is no underdrain, OR the lowest underdrain invert elevation | ELEVBMP |  | feet
| 8 | Groundwater elevation | ELEVGW |  | feet
| 9 | Depth to seasonal groundwater (Must be 2 feet or greater, or 3.5 feet or greater if draining to combined sewer) | DGW | 0 | feet
Section 3 BMP Specifications
| 10 | Dimensions of the permeable pavement (length, width, or area) | L |  | feet
|  |  | W |  | feet
|  |  | ABMP | 0 | square feet
| 11 | Depth of underlying aggregate (must be less than Dallow) | D1 |  | feet
| 12 | Aggregate porosity (0.38 maximum unless detailed materials report provided) | P1 |  | unitless
| 13 | Volume of Aggregate storage applicable to volume control = ABMP * D1*P1 | VBMP | 0 | cubic feet
Section 4 BMP Performance
| 14 | Volume of upstream runoff (Line 3) | Vupstream | 0 | cubic feet
| 15 | Volume Control Storage Provided = VBMP | VBMP | 0 | cubic feet
| 16 | Vtotal (equals lesser of VBMP or Vupstream) | Vtotal | 0 | cubic feet
Note on E13: On other BMP worksheets this calculation is performed to compute the total runoff from a 1-inch storm to the BMP including upstream pervious areas. Here it should only include impervious areas because pervious areas should not be routed to permeable pavement.

## 2.1.7.1 Roof Runoff Planters
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.7 Roof Runoff BMPs - Planter Boxes
Section 1 Upstream Drainage Area
| 1 | Upstream impervious area including BMP area | At |  | square feet
| 2 | Upstream weighted C-value (C-value=1.0 for bioinfiltration area for direct rainfall) | C |  | unitless
| 3 | Volume of upstream runoff from a 1-inch storm = C * At * 1/12 | Vupstream | 0 | cubic feet
| 4 | Describe system (Will planter box include aggregate, does it drain to underlying soils, is it underdrained to the stormater management system)
Section 2 BMP Feasibilty
| 5 | Design soil infiltration rate (must be 0.5 in/hr or greater if planter box is to drain to subsoil) | i |  | in/hr
| 6 | Elevation of bottom of BMP (the infiltration surface) IF there is no underdrain, OR the lowest underdrain invert elevation | ELEVBMP |  | feet
| 7 | Groundwater elevation | ELEVGW |  | feet
| 8 | Depth to seasonal groundwater (Must be 2 feet or greater, or 3.5 feet or greater if draining to combined sewer) | DGW | 0 | feet
Section 3 BMP Specifications
| 9 | Dimensions of the planter box (length, width, or area) | L |  | feet
|  |  | W |  | feet
|  |  | ABMP | 0 | square feet
| 10 | Depth of surface storage | D1
| 11 | Depth of prepared soil | D2 |  | feet
| 12 | Prepared soil porosity (0.25 maximum unless detailed materials report provided) | P2 |  | unitless
| 13 | Depth of underlying aggregate (optional) | D3 |  | feet
| 14 | Aggregate porosity (0.38 maximum unless detailed materials report provided) | P3 |  | unitless
| 15 | Air space storage volume (ABMP * D1) | VAIR | 0 | cubic feet
| 16 | Planter box soil media storage volume = ABMP * [(D2 * P2) + (D3 * P3)] | VSOIL | 0 | cubic feet
Section 4 BMP Performance
| 17 | Volume of upstream runoff (Line 4) | Vupstream | 0 | cubic feet
| 18 | Storage Provided = VAIR + VSOIL | VBMP | 0 | cubic feet
| 19 | Vtotal (equals lesser of VBMP or Vupstream) | Vtotal | 0 | cubic feet

## 2.1.7.2 Roof Runoff Rain Barrel
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.7 Roof Runoff BMPs - Rain Barrels / Cisterns
Section 1 Upstream Drainage Area
| 1 | Upstream impervious area | Ai |  | square feet
| 2 | Upstream weighted C-value | C |  | unitless
| 3 | Volume of upstream runoff from a 1-inch storm = C * At * 1/12 | Vupstream | 0 | cubic feet
| 4 | Describe system (Wwhat are the sizes and numbers of rain barrels or cisterns?)
Section 2 BMP Specifications
| 5 | List Rain Barrels and attach plan showing location and sizes of all rain barrels (Attach additional sheets if necessary) | Number / Designation | Volume
cubic feet
cubic feet
cubic feet
cubic feet
| 6 | Total capacity of rain barrels | VRB | 0 | cubic feet
| 7 | List Cisterns and attach plan showing location and sizes of all cisterns. (Attach additional sheets if necessary) | Number / Designation | Volume
cubic feet
cubic feet
cubic feet
cubic feet
| 8 | Total capacity of rain barrels | VCIS | 0 | cubic feet
| 9 | Total capacity of rain barrels or cisterns | VBMP = VRB + VCIS | 0 | cubic feet
Section 4 BMP Performance
| 10 | Volume of upstream runoff (Line 3) | Vupstream | 0 | cubic feet
| 11 | Storage Provided = VBMP | VBMP | 0 | cubic feet
| 12 | Vtotal (equals lesser of VBMP or Vupstream) | Vtotal | 0 | cubic feet

## 2.1.8 Filter Strips
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.8 Filter Strips Worksheet
Section 1 Upstream Drainage Area
| 1 | Upstream impervious area | Ai |  | square feet
| 2 | Volume of upstream runoff from a 1-inch storm = 0.95 * Ai * 1/12 | Vupstream | 0 | cubic feet
| 3 | Describe upstream drainage area
Section 2 BMP Feasibilty
| 4 | Elevation of filter strip surface | ELEVBMP |  | feet
| 5 | Groundwater elevation | ELEVGW |  | feet
| 6 | Depth to seasonal groundwater (Must be 2 feet or greater, or 3.5 feet or greater if draining to combined sewer) | DGW | 0 | feet
Section 3 BMP Specifications
| 7 | Dimensions of the filter strip [length L (length parallel to flow must be 20% or greater than the DA flowpath), width W, slope] | L |  | feet
|  |  | W |  | feet
|  |  | Slope (1% to 5%) |  | %
| 8 | Check effective tributary flow length (must be less than 75 feet and level spreader required if not a uniformly sloping surface) Effective flow path of drainage area = Ai/W | DA Flowpath | #DIV/0! | feet
| 9 | If minimum design requirements are met, compute minimum impervious area for which swale serves as volume control. Impervious Area controlled = Filter strip area (L * W) | Impervious Area Controlled | 0 | square feet
Section 4 BMP Performance
| 10 | Volume of upstream impervious area runoff (Line 2) | Vupstream | 0 | cubic feet
| 11 | Equivalent Volume Control Storage (V = Area Controlled * 0.5 / 12) | VBMP | 0 | cubic feet
| 12 | Vtotal (equals lesser of VBMP or Vupstream) | Vtotal | 0 | cubic feet
Note on E21: Must be 20% or greater than DA Flowpath
Note on E24: Flowpath length to filter strip must be equivalent to 75 feet or less. If not uniformly sloping, or if concentrated discharge such as roof runoff is being discharged, level spreader is required.

## 2.1.9 Oversized Detention
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1.9 Oversized Detention Worksheet
You must first complete Tab 1.0 Rate Control and Tab 2.0 Volume Control worksheets to use this Oversized Detention Worksheet.
Step 1: | Oversized Detention Computation |  |  | Units | Notes
|  | Maximum Release Rate for Rate Control (automatically entered from cell G72 on Rate Control worksheet) | 0 | cfs
|  | Rate Control Storage | 0 | cubic feet
|  | Volume Control Storage | 0 | cubic feet
|  | Total Storage Required for oversized detention | 0 | cubic feet
|  | Try reducing release rate here until total required storage in oversized detention facility is achieved. |  | cfs
|  | Total Storage Provided |  | cubic feet
Oversized Detention Calculation
(Based on Bulletin 75 Rainfall Data)
STORM EVENT (5,10,25,50 or 100) =
|  | 100 |  |  |  | 0 | cfs
|  |  |  | Infow |  | Release | Storage | Storage
Storm | Runoff | Rainfall | Drainage | Rate | Total | Rate | Rate | Volume Rate
Duration | Coefficient | Intensity | Area A | Q=CIA | Storm Vol | Qo | Qi-Qo | (Qi-Qo)*t*60
(minutes) | C | (in/hr) | (acres) | (cfs) | (cu ft) | (cfs) | (cfs) | (cu ft)
5 | 0 | 12.36 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 9.28 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 6.34 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 4.03 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0 | 2.485 | 0 | 0 | 0 | 0 | 0 | 0
180 | 0 | 1.83 | 0 | 0 | 0 | 0 | 0 | 0
360 | 0 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0
720 | 0 | 0.62167 | 0 | 0 | 0 | 0 | 0 | 0
1080 | 0 | 0.44778 | 0 | 0 | 0 | 0 | 0 | 0
1440 | 0 | 0.35708 | 0 | 0 | 0 | 0 | 0 | 0
2880 | 0 | 0.19333 | 0 | 0 | 0 | 0 | 0 | 0
4320 | 0 | 0.13681 | 0 | 0 | 0 | 0 | 0 | 0
7200 | 0 | 0.088833 | 0 | 0 | 0 | 0 | 0 | 0
14400 | 0 | 0.052708 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Required Detention Vol (cf) | 0
Note: 1) the calculation assumes that the rising and recessing limb of inflow and outflow hydrograph are vertical
Note on G26: Uses Value entered in Cell D18

## 2.1 BMP Volume Summary
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
2.1 BMP Volume Summary
City of Chicago Stormwater Management
Summary of Volume Control BMP Storage
(Adds net allowable volume control storage from all worksheets)
| BMPs | Volume Control Storage Provided (cubic feet)
| Bioinfiltration Systems | 0
| Drainage Swales | 0
| Green Roof | -
| Detention (Infiltration Vaults) | 0
| Natural Landscaping and Stormwater Trees | -
| Permeable Paving | 0
| Roof Runoff BMPs - Planter Boxes | 0
| Roof Runoff BMPs - Rain Barrels and Cisterns | 0
| Vegetated Filter Strips | 0
| Total Provided | 0
| Storage Required if % Impervious Reduction is not met (from 2.0 Volume Control) | 0
Note on C17: Works to reduce effective impervious area, which reduced required storage. Not treated as storage itself.
Note on C19: Works to reduce effective impervious area, which reduced required storage. Not treated as storage itself.

## 3.0 Sustainable Development
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
3.0 Sustainable Development Policy
Chicago Sustainable Development Policy Stormwater Spreadsheet Summary
Instructions for use:
This summary worksheet provides information related to the Chicago Sustainable Development Policy, updated 2017.
The six sustainable development strategies related to stormwater are listed below with a detailed explanation of each strategy.
Not all projects within the City of Chicago are requried to comply with the Sustainable Development Policy. Check with the project
design team or the Department of Planning and Development to determine applicability.
To qualify for these strategies, the project must be a regulated development under the Stormwater Ordinance, except for strategy 3.4 Sump Pump Capture & Reuse.
| Type "Yes" to Select Strategy | Sustainable Development Strategy | Points | Explanation of Strategy | Instructions | Points Attempted
|  | 3.1 Exceed Stormwater Ordinance by 25% | 10 | The stormwater management plan must provide storage for 125% of the volume required by both the Rate Control and Volume Control components of the City of Chicago’s Stormwater Ordinance. Rate Control: The required Rate Control volume is calculated in the typical manner. Storage must be provided for 125% of this required volume. The release rate must be reduced in order to completely fill the volume provided. Volume Control: The required Volume Control volume is calculated in the typical manner. Storage must be provided for 125% of this required volume. This strategy does not apply when the Volume Control requirement is met through a 15% impervious area reduction. |  |  | 0
|  | 3.2 Exceed Stormwater Ordinance by 50% | 20 | The stormwater management plan must provide storage for 150% of the volume required by both the Rate Control and Volume Control components of the City of Chicago’s Stormwater Ordinance. Rate Control: The required Rate Control volume is calculated in the typical manner. Storage must be provided for 150% of this require volume. The release rate must be reduced in order to completely fill the volume provided. Volume Control: The required Volume Control volume is calculated in the typical manner. Storage must be provided for 150% of this required volume. This strategy does not apply when the Volume Control requirement is met through a 15% impervious area reduction. |  |  | 0
|  | 3.3 100% Stormwater Infiltration | 40 | The stormwater management plan must manage stormwater by discharging 100% of the stormwater into the ground through infiltration or by a combination of infiltration and stormwater capture and re-use. Geotechnical investigation including soil borings and infiltration testing will be required to confirm the presence of sandy soil on the site and establish an adequate infiltration rate. No stormwater discharge to the combined sewer system, Waters or adjacent property will be allowed for any storm less than a 100-year critical duration storm. |  |  | 0
|  | 3.4 Sump Pump Capture & Reuse | 5 | The stormwater management plan must indicate that all sump pumps will be discharged to an infiltration BMP, a stormwater capture and re-use facility or the detention system.
|  | 3.5 100-year Detention for Lot-to-lot Buildings | 5 | For a lot-to-lot building, provide detention (Rate Control) for the 100-year storm instead of the 10-year storm. A lot-to-lot building is defined as a building with 85% or more lot coverage. |  |  | 0
|  | 3.6 100-year Detention for Bypass | 5 | For sites with significant off-site tributary flow, provide detention (Rate Control) for the 100-year storm instead of the 25-year storm.
[5 empty] | Total Points Attempted | 0 | 0

## 3.1 Exceed Rate Control
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
3.1 Exceed Rate Control
You must first complete Tab 1.0 Rate Control and Tab 3.0 Sustainable Development Policy worksheets to use this worksheet.
Step 1: | Exceed Detention Computation |  |  | Units | Notes
|  | Maximum Release Rate for Rate Control (automatically entered from cell G73 on Rate Control worksheet) | 0 | cfs
|  | Rate Control Storage to meet the Stormwater Ordinance | 0 | cu ft
|  | Percent exceeding |  | percent
|  | Total Rate Control Storage Required to exceed the Stormwater Ordinance |  | cu ft
|  | Try reducing release rate here until total required storage in oversized detention facility is achieved. |  | cfs
|  | Total Storage Provided |  | cu ft
Exceed Detention Calculation
(Based on Bulletin 75 Rainfall Data)
STORM EVENT (5,10,25,50 or 100) =
|  | 100 |  |  |  | 0 | cfs
|  |  | Drainage | Infow |  | Release | Storage | Storage
Storm | Runoff | Rainfall | Area | Rate | Total | Rate | Rate | Volume Rate
Duration | Coefficient | Intensity | A | Q=CIA | Storm Vol | Qo | Qi-Qo | (Qi-Qo)*t*60
(minute) | C | (in/hr) | (acres) | (cfs) | (cu ft) | (cfs) | (cfs) | (cu ft)
5 | 0 | 12.36 | 0 | 0 | 0 | 0 | 0 | 0
10 | 0 | 10.8 | 0 | 0 | 0 | 0 | 0 | 0
15 | 0 | 9.28 | 0 | 0 | 0 | 0 | 0 | 0
30 | 0 | 6.34 | 0 | 0 | 0 | 0 | 0 | 0
60 | 0 | 4.03 | 0 | 0 | 0 | 0 | 0 | 0
120 | 0 | 2.485 | 0 | 0 | 0 | 0 | 0 | 0
180 | 0 | 1.83 | 0 | 0 | 0 | 0 | 0 | 0
360 | 0 | 1.0717 | 0 | 0 | 0 | 0 | 0 | 0
720 | 0 | 0.62167 | 0 | 0 | 0 | 0 | 0 | 0
1080 | 0 | 0.44778 | 0 | 0 | 0 | 0 | 0 | 0
1440 | 0 | 0.35708 | 0 | 0 | 0 | 0 | 0 | 0
2880 | 0 | 0.19333 | 0 | 0 | 0 | 0 | 0 | 0
4320 | 0 | 0.13681 | 0 | 0 | 0 | 0 | 0 | 0
7200 | 0 | 0.088833 | 0 | 0 | 0 | 0 | 0 | 0
14400 | 0 | 0.052708 | 0 | 0 | 0 | 0 | 0 | 0
[7 empty] | Required Detention Vol (cf) | 0
Note: 1) the calculation assumes that the rising and recessing limb of inflow and outflow hydrograph are vertical
Note on G26: Uses Value entered in Cell D18

## 3.2 Exceed Volume Control
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
3.2 Exceed Volume Control
You must first complete Tab 2.0 Volume Control and Tab 3.0 Sustainable Development Policy worksheets to use this worksheet.
| Exceed Volume Control Computation |  |  | Units | Notes
|  | Volume Control Storage to meet the Stormwater Ordinance | 0 | cubic feet
|  | Percent exceeding |  | percent
|  | Total Volume Control Storage Required to exceed the Stormwater Ordinance |  | cubic feet

## IDF
City of Chicago
Department of Water Management
Name of Project:
Address:
A/E of Record:
(FOR COMPUTATIONS AND REFERENCE)
City of Chicago Intensity-Duration-Frequency (IDF) Curve
(Based Bulletin 75 Rainfall Data)
Storm Event in Years
|  |  | 5 |  | 10 |  | 25 |  | 50 |  | 100
|  | 5-Year |  | 10-Year |  | 25-Year |  | 50-Year |  | 100-Year
|  | 20% Annual Chance |  | 10% Annual Chance |  | 4% Annual Chance |  | 2% Annual Chance |  | 1% Annual Chance
| Storm Duration (min) | Rainfall (in) | Average Intensity (in/hr) | Rainfall (in) | Average Intensity (in/hr) | Rainfall (in) | Average Intensity (in/hr) | Rainfall (in) | Average Intensity (in/hr) | Rainfall (in) | Average Intensity (in/hr)
5 minute | 5 | 0.52 | 6.24 | 0.62 | 7.44 | 0.77 | 9.24 | 0.9 | 10.8 | 1.03 | 12.36
10 minute | 10 | 0.9 | 5.4 | 1.08 | 6.48 | 1.35 | 8.1 | 1.58 | 9.48 | 1.8 | 10.8
15 minute | 15 | 1.16 | 4.64 | 1.39 | 5.56 | 1.74 | 6.96 | 2.03 | 8.12 | 2.32 | 9.28
30 minute | 30 | 1.59 | 3.18 | 1.91 | 3.82 | 2.39 | 4.78 | 2.78 | 5.56 | 3.17 | 6.34
1 hour | 60 | 2.02 | 2.02 | 2.42 | 2.42 | 3.03 | 3.03 | 3.53 | 3.53 | 4.03 | 4.03
2 hours | 120 | 2.49 | 1.245 | 2.99 | 1.495 | 3.74 | 1.87 | 4.35 | 2.175 | 4.97 | 2.485
3 hours | 180 | 2.75 | 0.91667 | 3.3 | 1.1 | 4.13 | 1.3767 | 4.8 | 1.6 | 5.49 | 1.83
6 hours | 360 | 3.23 | 0.53833 | 3.86 | 0.64333 | 4.84 | 0.80667 | 5.63 | 0.93833 | 6.43 | 1.0717
12 hours | 720 | 3.74 | 0.31167 | 4.48 | 0.37333 | 5.61 | 0.4675 | 6.53 | 0.54417 | 7.46 | 0.62167
18 hours | 1080 | 4.04 | 0.22444 | 4.84 | 0.26889 | 6.06 | 0.33667 | 7.05 | 0.39167 | 8.06 | 0.44778
24 hours | 1440 | 4.3 | 0.17917 | 5.15 | 0.21458 | 6.45 | 0.26875 | 7.5 | 0.3125 | 8.57 | 0.35708
48 hours | 2880 | 4.71 | 0.098125 | 5.62 | 0.11708 | 6.99 | 0.14563 | 8.13 | 0.16937 | 9.28 | 0.19333
72 hours | 4320 | 5.08 | 0.070556 | 6.05 | 0.084028 | 7.49 | 0.10403 | 8.64 | 0.12 | 9.85 | 0.13681
5 days | 7200 | 5.63 | 0.046917 | 6.68 | 0.055667 | 8.16 | 0.068 | 9.39 | 0.07825 | 10.66 | 0.088833
10 days | 14400 | 7.09 | 0.029542 | 8.25 | 0.034375 | 9.9 | 0.04125 | 11.26 | 0.046917 | 12.65 | 0.052708